Cold Climate- temperature controller

Setting the set point (desired temperature)

• Press SET for 1 sec, the set value will start flashing.

. • Use the UP / DOWN buttons to set the new required temperature

• Press SET to confirm the new temperature.

How to adjust the defrost parameters:

1. Press SET for 3 seconds (the display will show “PS”).

2. Enter the password “22” using UP/DOWN buttons and press set.

3. Use the UP/DOWN buttons to scroll through the menu until the require parameter is shown and press set.

4. Scroll UP/DOWN buttons to select the require parameter

5. Press SET to confirm the changes (back to the parameter menu).

6. Press SET for 3 seconds to save the new values and exit the menu. ,.

Defrost parameters list:

D4-0

D5-0

D6-0

DI- Interval between defrosts (every 1 hour)

DT- End defrost temperature (6 degrees)

DP Max defrost duration (7 minutes)

DD- dripping time (1 minute if necessary)